## HeaderMap
client_header | canonical_field | note
Aantal | aantal | Real header, already covered by DEFAULT_HEADER_MAP -- listed here for completeness only.
Omschrijving | omschrijving | Real header, already covered by DEFAULT_HEADER_MAP.
Veldapparatuur | fabricaat | UNCONFIRMED -- blank in every visible row. Best-guess by name only.
Regelpaneel | rk | UNCONFIRMED -- blank in every visible row. Best-guess by name only.
B | DI_bedrijf | Bedrijf feedback. Confirmed: every pump/Tracing row using this column is a genuine bedrijf-type contact -- this is what DI_bedrijf was built for, not a repurposed slot.
ST | DI_storing | Storing feedback. Confirmed on every pump row (paired with DO) and standalone on Brandmelding/Fasebewakingsrelais/Rookmelder kanaal.
DI | DI | Direct -- simple digital input (Reset storing).
AI | AI | Direct -- confirmed on every sensor row.
DO | DO | Direct -- primary DO source.
AO | AO | Direct -- primary AO source.
Protocol | bus_protocol | Direct, real protocol-name column -- unlike RK Lob C, this layout can derive bus_protocol properly. No rows in the visible sample are populated, but the column is real.
DO_1 | opmerking | Confirmed: interventie marker (Priva BlueID DOR4m/DOR8m -- "met handmatige bediening, 3 interventieknoppen per uitgang"), not a second DO signal. Routed to opmerking so it stays visible for panel-BOM purposes without affecting cable derivation. Does NOT need the DO_2 code change -- that fix is still needed for RK Lob C (DI_2/DU_3), just not for this project.
AO_2 | opmerking | Confirmed: interventie marker (Priva BlueID AO4m -- same "met handmatige bediening" pattern as DO_1). Not a second AO signal. Routed to opmerking, same as DO_1. The AO_2 code change proposed earlier is NOT needed for this project -- struck from the dependency list below.
NOT MAPPED:
Left unmapped, deliberately: IW / VW: bare point-count pair (Ingangswaarde/Verzendwaarde), same shape as RK Lob C's Buscommunicatie/Column6. Unlike RK Lob C, this layout ALSO has a real Protocol column, so bus_protocol does not depend on these -- no loss here.
DEPENDENCIES BEFORE TESTING:
THIS PROJECT NEEDS, BEFORE TESTING: 1. The group-header zero-check fix (add DI_bedrijf/DI_storing/DI_status to the check tuple) -- CONFIRMED NECESSARY: Brandmelding and Fasebewakingsrelais have ONLY a DI_storing-bound (ST) signal and nothing in plain AI/AO/DI/DO/SOFT, so without this fix they get silently swallowed as group headers -- a fire-detection row disappearing without a flag. 2. Nothing else. DO_1 and AO_2 turned out to be Priva BlueID interventie markers (DOR4m/DOR8m/AO4m "met handmatige bediening"), not second signal sources -- both route to opmerking now. The DO_2 code change is still needed for RK Lob C separately, and the AO_2 code change proposed earlier is cancelled -- not needed anywhere so far.

## valid_fields
canonical_field
rk
group
procescode
omschrijving
fabricaat
type
aantal
AI
AO
DI
DO
SOFT
voltage
power_kw
current_a
va
bus_protocol
bus_naam
derden_flag
locatie
regelkast_spec
opmerking
source_ref